## Public Tool
TAPIR Public Decision-Support Tool
Select a case to see the preferred pathway, actor scores and the essential evidence at a glance
SELECTED CASE |  | Walcheren
Response-option ranking | [6 empty] | Preferred response option
Response option |  |  | Stedin | Company | Equal actor average |  | Battery + EMS
Conventional grid reinforcement |  |  | 2.85 | 2.5 | 2.675
Battery + EMS |  |  | 3.975 | 4.45 | 4.2125 |  | Grid operator 04 / 5 ¦ Company 04 / 5 ¦ Overall 04 / 5
Group Transport Agreement |  |  | 3.05 | 3.3 | 3.175 |  | Short peaks at the high-voltage station are reduced below the threshold by both flexibility solutions. The margins are narrow, and performance over the full period remains uncertain without a forward series.
No additional intervention |  |  | 3.05 | 2.7 | 2.875
Case context - public village demand indicators and percentage-only station load
Public village label |  | Village data coverage |  | Average daily demand |  | Village maximum peak |  | Peak period at annual maximum |  | Peak-period average
Village 2 |  | 1 |  | 29171.2 |  | 3644.4 |  | Christmas holiday |  | 48505.2
Grid level |  | ATC stress 2025 |  | ATC stress 2031 |  | First constraint year |  | Hours at or above 90% (total / holiday) |  | Holiday share of those hours
Distribution / MS level |  | 63.4% |  | 82.3% |  | 2035 |  | 0 total / 0 holiday |  | N/A
Main Distribution Station level |  | 94.8% |  | >100% |  | 2025 |  | 4.25 total / 1.75 holiday |  | 41.2%
Threshold 90% |  | Both flexibility solutions clear the 90% threshold in the measured test
The high-voltage percentage is a 2025 measurement; no forward forecast series exists for that level because reinforcement follows in the short term. The distribution-level percentage is the 2031 forecast. Flexibility lowers the high-voltage level to 88.3% (battery + EMS) and 89.1% (Group Transport Agreement).
TAPIR-adjusted criteria and selected-case scores
Actor | Criterion |  | Weight | TAPIR factor | Conventional grid reinforcement | Battery + EMS | Group Transport Agreement | No additional intervention | KPI / evidence applied |  | Case specific adjustments
Grid operator | Grid-operator life-cycle cost and investment effect |  | 30% | Economic prospects | 2 | 4.5 | 4.5 | 5 | Reinforcement investment cost (EUR), identified flexibility cost and years of deferred reinforcement investment; no complete discounted life-cycle cost |  | Battery +0.5 — clears the threshold: ATC 0.948 → 0.883. ¦ GTO +0.5 — clears the threshold: ATC 0.948 → 0.891.
Grid operator | Timing, duration, reliability and predictability |  | 20% | Maturity | 3.5 | 2.5 | 2.5 | 1 | Critical hours, holiday overlap, availability, asset life |  | Grid −0.5 — constrained since 2025; reinforcement only end 2028. ¦ Battery +0.5 — stress in 4.25 h a year, episodes of about one hour. ¦ GTO −0.5 — collective maturity 2 of 5; initiatives are knowledge exchange only.
Grid operator | Speed and effect on reinforcement bridge gap |  | 20% | Feasibility | 1 | 5 | 3 | 1.5 | Constraint year, reinforcement year, bridge period, station peak relief, ATC <= 0.90 and years actually bridged |  | Battery +0.5 — clears 0.90 and covers 3 of the 3 bridge years. ¦ Exit −0.5 — peak stays at 0.948 for all three years.
Grid operator | Technical and operational readiness |  | 15% | Maturity | 5 | 4.5 | 2 | 2 | Battery/EMS installed, control systems, GTO status |  | Battery +0.5 — several companies already operate batteries with EMS.
Grid operator | Legal, contractual and policy embeddedness |  | 15% | Local embeddedness | 4 | 3 | 2 | 5 | Legal status, agreements, connection conditions, policy alignment
Company | Financial attractiveness |  | 30% | Economic prospects | 2 | 5 | 4.5 | 2 | Cost, annual benefit, payback, grid charges, GTO compensation |  | Battery +0.5 — payback accepted where cost-neutral and capacity is delivered. ¦ GTO +0.5 — clears the threshold without company capital expenditure.
Company | Implementation speed and urgency fit |  | 20% | Feasibility | 1 | 4.5 | 3 | 1 | Constraint year, reinforcement date, case-specific lead time and availability before the constraint |  | Battery +0.5 — available well before the end of 2028.
Company | Knowledge and organisational burden |  | 20% | Scalability + feasibility | 4 | 3.5 | 1.5 | 5 | Advice needed, actors involved, management time, coordination |  | Battery +0.5 — battery and EMS operation already established locally. ¦ GTO −0.5 — collective work is company-led; coordination falls on the companies.
Company | Autonomy and dependency |  | 15% | Regional relatedness + local embeddedness | 3 | 5 | 2 | 5 | Asset control, dependence on others, collective decisions
Company | Sustainability, image and strategic risk |  | 15% | Climate and energy impacts | 3 | 4 | 5 | 1 | Electrification, PV and storage use, policy and strategy fit
Interpretation and public-use note
Response option is the umbrella term for the four alternatives. Battery + EMS and the Group Transport Agreement are the flexibility-solution subset; conventional grid reinforcement and no additional intervention are not flexibility solutions.
Flexibility is assessed as a possible complement to or bridge towards reinforcement. It is not assumed to replace reinforcement where the percentage-based grid evidence indicates that physical capacity remains necessary.
Score precision: every score is displayed to one decimal place (for example 3.7 / 5, not 4) and the same precision applies to all three cases. The underlying values are the full weighted results and are not rounded before display.
Village demand indicators are public tourism-demand data and are shown in full. Confidentiality applies only to identifiers and absolute grid values: the workbook contains no village names, station names or codes, no absolute station load, capacity or relief values, no exact project costs or dates, no internal source filenames, no hidden sheets and no external links.

## Public Inputs
Public TAPIR Inputs and Scoring Logic
Public version: village demand indicators are shown in full; village names, station names and all absolute grid load/capacity values are removed
Editable base criteria, weights and response-option scores | [12 empty] | Case-specific pathway result library
Actor | Criterion | Weight | TAPIR factor | KPI / evidence basis | Conventional grid reinforcement | Battery + EMS | Group Transport Agreement | No additional intervention |  |  |  |  | Case region | Response option | Grid-operator score | Company score | Equal actor average | Result | Lookup key
Grid operator | Grid-operator life-cycle cost and investment effect | 30% | Economic prospects | Relative investment implications, flexibility cost and potential reinforcement deferral; absolute project values are excluded. | 2 | 4 | 4 | 5 |  |  |  |  | Schouwen-Duiveland | Conventional grid reinforcement | 2.85 | 2.5 | 2.675 | - | Schouwen-Duiveland¦Conventional grid reinforcement
Grid operator | Timing, duration, reliability and predictability | 20% | Maturity | Threshold exceedance pattern, timing, availability and asset life, expressed without absolute load data. | 4 | 2 | 3 | 1 |  |  |  |  | Schouwen-Duiveland | Battery + EMS | 3.65 | 4.25 | 3.95 | Preferred response option | Schouwen-Duiveland¦Battery + EMS
Grid operator | Speed and effect on reinforcement bridge gap | 20% | Feasibility | Whether an option is available during the bridge period and reduces ATC stress to 90% or below. | 1 | 5 | 3 | 2 |  |  |  |  | Schouwen-Duiveland | Group Transport Agreement | 3.075 | 3.425 | 3.25 | - | Schouwen-Duiveland¦Group Transport Agreement
Grid operator | Technical and operational readiness | 15% | Maturity | Installed assets, control systems and the operational status of flexibility arrangements. | 5 | 4 | 2 | 2 |  |  |  |  | Schouwen-Duiveland | No additional intervention | 3.05 | 2.7 | 2.875 | - | Schouwen-Duiveland¦No additional intervention
Grid operator | Legal, contractual and policy embeddedness | 15% | Local embeddedness | Legal status, agreements, connection conditions and policy alignment. | 4 | 3 | 2 | 5 |  |  |  |  | Walcheren | Conventional grid reinforcement | 2.85 | 2.5 | 2.675 | - | Walcheren¦Conventional grid reinforcement
Company | Financial attractiveness | 30% | Economic prospects | Relative cost, benefit, payback and compensation considerations; confidential monetary values are excluded. | 2 | 5 | 4 | 2 |  |  |  |  | Walcheren | Battery + EMS | 3.975 | 4.45 | 4.2125 | Preferred response option | Walcheren¦Battery + EMS
Company | Implementation speed and urgency fit | 20% | Feasibility | Case-specific lead time and availability before the constraint becomes binding. | 1 | 4 | 3 | 1 |  |  |  |  | Walcheren | Group Transport Agreement | 3.05 | 3.3 | 3.175 | - | Walcheren¦Group Transport Agreement
Company | Knowledge and organisational burden | 20% | Scalability + feasibility | Advice needs, actors involved, management time and coordination requirements. | 4 | 3 | 2 | 5 |  |  |  |  | Walcheren | No additional intervention | 3.05 | 2.7 | 2.875 | - | Walcheren¦No additional intervention
Company | Autonomy and dependency | 15% | Regional relatedness + local embeddedness | Asset control, dependence on other actors and collective decision requirements. | 3 | 5 | 2 | 5 |  |  |  |  | West-Zeeuws-Vlaanderen | Conventional grid reinforcement | 2.85 | 2.5 | 2.675 | - | West-Zeeuws-Vlaanderen¦Conventional grid reinforcement
Company | Sustainability, image and strategic risk | 15% | Climate and energy impacts | Electrification, renewable-energy use, policy alignment and strategic fit. | 3 | 4 | 5 | 1 |  |  |  |  | West-Zeeuws-Vlaanderen | Battery + EMS | 3.8 | 4.35 | 4.075 | Preferred response option | West-Zeeuws-Vlaanderen¦Battery + EMS
[13 empty] | West-Zeeuws-Vlaanderen | Group Transport Agreement | 2.975 | 3.225 | 3.1 | - | West-Zeeuws-Vlaanderen¦Group Transport Agreement
Weight validation | Grid operator | 100% | Company | 100% | OK — both actors total 100% | [7 empty] | West-Zeeuws-Vlaanderen | No additional intervention | 3.05 | 2.7 | 2.875 | - | West-Zeeuws-Vlaanderen¦No additional intervention
Anonymised case indicators — load values expressed only as percentages | [12 empty] | Selected-case adjustment summaries | [6 empty] | Public village demand indicators and two-station percentage load indicators
Case region | Public village label | Data coverage |  | Distribution / MS-level station: peak as % of capacity | High-voltage station: baseline peak as % of capacity | High-voltage station: after battery + EMS | High-voltage station: after Group Transport Agreement | Evidence basis | Threshold result | Public grid summary | Interview synthesis | Public-data note | Case region | Criterion | Public adjustment summary | Lookup key |  |  |  | Village data coverage | Village average daily demand (kWh/day) | Village maximum peak (kW) | Peak period containing the annual maximum | Peak-period average daily demand (kWh/day) | MS ATC stress 2025 | MS ATC stress 2031 | MS first constraint year | MS critical hours at or above 90% | MS holiday share of critical hours | HVS ATC stress 2025 | HVS ATC stress 2031 | HVS first constraint year | HVS critical hours at or above 90% | HVS holiday share of critical hours | Scenario and evidence-year note
Schouwen-Duiveland | Village 1 | 100% |  | 88.7% | 97% | 91.4% | 91.6% | Forecast percentage | Neither flexibility solution clears the 90% threshold | The high-voltage station is forecast to exceed the threshold before planned reinforcement. Both flexibility solutions reduce stress, but neither removes the exceedance; reinforcement therefore remains necessary. | Interview synthesis indicates that existing regional cooperation may lower the coordination burden for a collective agreement, while companies continue to value autonomy and options that can be implemented quickly. | All load and capacity indicators are normalised percentages. Absolute electrical values, station identifiers and exact project inputs have been removed. | Schouwen-Duiveland | Grid-operator life-cycle cost and investment effect | Base score unchanged for this criterion. | Schouwen-Duiveland¦Grid-operator life-cycle cost and investment effect |  |  |  | 100% | 43062 | 5049.6 | Christmas holiday | 67345.2 | 66.6% | 88.7% | N/A | 0 total / 0 holiday | N/A | 76.2% | 97% | 2031 | 10 total / 7 holiday | 70% | Both percentages are forecast values. The distribution-level percentage cannot be reproduced from the forecast series at the stated capacity, so its evidence year is unresolved; the high-voltage percentage is the 2031 forecast. Flexibility lowers the high-voltage level to 91.4% (battery + EMS) and 91.6% (Group Transport Agreement), so neither clears 90%.
Walcheren | Village 2 | 100% |  | 82.3% | 94.8% | 88.3% | 89.1% | Measured percentage test | Both flexibility solutions clear the 90% threshold in the measured test | Short peaks at the high-voltage station are reduced below the threshold by both flexibility solutions. The margins are narrow, and performance over the full period remains uncertain without a forward series. | Interview synthesis indicates that battery and EMS operation is already established at several companies. Collective initiatives are less mature and place more coordination responsibility on participating companies. | All load and capacity indicators are normalised percentages. Absolute electrical values, station identifiers and exact project inputs have been removed. | Schouwen-Duiveland | Timing, duration, reliability and predictability | Reinforcement follows a short bridge period while the binding-component stress exceeds the 90% threshold. | Schouwen-Duiveland¦Timing, duration, reliability and predictability |  |  |  | 100% | 29171.2 | 3644.4 | Christmas holiday | 48505.2 | 63.4% | 82.3% | 2035 | 0 total / 0 holiday | N/A | 94.8% | >100% | 2025 | 4.25 total / 1.75 holiday | 41.2% | The high-voltage percentage is a 2025 measurement; no forward forecast series exists for that level because reinforcement follows in the short term. The distribution-level percentage is the 2031 forecast. Flexibility lowers the high-voltage level to 88.3% (battery + EMS) and 89.1% (Group Transport Agreement).
West-Zeeuws-Vlaanderen | Village 3 | 84.11% |  | 53.9% | 90.6% | 86.1% | 85.8% | Measured percentage test | Both flexibility solutions clear the 90% threshold initially; future coverage is uncertain | The high-voltage station marginally exceeds the threshold in the measured profile. Both flexibility solutions clear the threshold initially, but the longer-term result and the link to reinforcement remain uncertain. | Interview synthesis indicates that batteries are under consideration, whereas central company decision structures and limited collective governance increase the coordination burden for a Group Transport Agreement. | All load and capacity indicators are normalised percentages. Absolute electrical values, station identifiers and exact project inputs have been removed. | Schouwen-Duiveland | Speed and effect on reinforcement bridge gap | No relief is provided during the bridge period; the baseline ATC stress remains 97.0%. | Schouwen-Duiveland¦Speed and effect on reinforcement bridge gap |  |  |  | 100% | 9414.6 | 1450 | N/A - annual peak outside the defined periods | N/A | 43% | 53.9% | N/A | 0 total / 0 holiday | N/A | 90.6% | >100% | 2029 | 1 total / 0 holiday | Not derived | The high-voltage percentage is a 2025 measurement; the holiday split of the single critical hour was not derived. The distribution-level percentage is the earliest available forecast year (2026) rather than 2031, and that level stays below capacity across the forecast horizon. Flexibility lowers the high-voltage level to 86.1% (battery + EMS) and 85.8% (Group Transport Agreement).
[13 empty] | Schouwen-Duiveland | Technical and operational readiness | Regional energy cooperation is developing, which improves the relative readiness of a collective arrangement. | Schouwen-Duiveland¦Technical and operational readiness
Case-specific regional adjustments and transparent score calculation | [12 empty] | Schouwen-Duiveland | Legal, contractual and policy embeddedness | Base score unchanged for this criterion. | Schouwen-Duiveland¦Legal, contractual and policy embeddedness
Case region | Actor | Criterion | Response option | Regional adjustment | Public evidence | Evidence type | Calculation key | Base score | Weight | Adjusted score | Weighted contribution |  | Schouwen-Duiveland | Financial attractiveness | Base score unchanged for this criterion. | Schouwen-Duiveland¦Financial attractiveness
Schouwen-Duiveland | Grid operator | Grid-operator life-cycle cost and investment effect | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Grid-operator life-cycle cost and investment effect¦Conventional grid reinforcement | 2 | 30% | 2 | 0.6 |  | Schouwen-Duiveland | Implementation speed and urgency fit | Base score unchanged for this criterion. | Schouwen-Duiveland¦Implementation speed and urgency fit
Schouwen-Duiveland | Grid operator | Grid-operator life-cycle cost and investment effect | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Grid-operator life-cycle cost and investment effect¦Battery + EMS | 4 | 30% | 4 | 1.2 |  | Schouwen-Duiveland | Knowledge and organisational burden | Regional groups and municipal facilitation can reduce the coordination burden. | Schouwen-Duiveland¦Knowledge and organisational burden
Schouwen-Duiveland | Grid operator | Grid-operator life-cycle cost and investment effect | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Grid-operator life-cycle cost and investment effect¦Group Transport Agreement | 4 | 30% | 4 | 1.2 |  | Schouwen-Duiveland | Autonomy and dependency | Existing cooperation reduces the dependency objection identified by participating companies. | Schouwen-Duiveland¦Autonomy and dependency
Schouwen-Duiveland | Grid operator | Grid-operator life-cycle cost and investment effect | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Grid-operator life-cycle cost and investment effect¦No additional intervention | 5 | 30% | 5 | 1.5 |  | Schouwen-Duiveland | Sustainability, image and strategic risk | Base score unchanged for this criterion. | Schouwen-Duiveland¦Sustainability, image and strategic risk
Schouwen-Duiveland | Grid operator | Timing, duration, reliability and predictability | Conventional grid reinforcement | -0.5 | Reinforcement follows a short bridge period while the binding-component stress exceeds the 90% threshold. | Percentage-based grid assessment | Schouwen-Duiveland¦Grid operator¦Timing, duration, reliability and predictability¦Conventional grid reinforcement | 4 | 20% | 3.5 | 0.7 |  | Walcheren | Grid-operator life-cycle cost and investment effect | The measured ATC stress decreases from 94.8% to 88.3%, below the 90% threshold. ¦ The measured ATC stress decreases from 94.8% to 89.1%, below the 90% threshold. | Walcheren¦Grid-operator life-cycle cost and investment effect
Schouwen-Duiveland | Grid operator | Timing, duration, reliability and predictability | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Timing, duration, reliability and predictability¦Battery + EMS | 2 | 20% | 2 | 0.4 |  | Walcheren | Timing, duration, reliability and predictability | The component is already constrained and reinforcement follows only after a bridge period. ¦ The measured exceedance consists of short episodes, improving the fit of targeted storage dispatch. ¦ Collective initiatives are at an early stage and are primarily focused on knowledge exchange. | Walcheren¦Timing, duration, reliability and predictability
Schouwen-Duiveland | Grid operator | Timing, duration, reliability and predictability | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Timing, duration, reliability and predictability¦Group Transport Agreement | 3 | 20% | 3 | 0.6 |  | Walcheren | Speed and effect on reinforcement bridge gap | The battery test clears the 90% threshold during the available bridge period. ¦ No intervention leaves the measured ATC stress at 94.8% throughout the bridge period. | Walcheren¦Speed and effect on reinforcement bridge gap
Schouwen-Duiveland | Grid operator | Timing, duration, reliability and predictability | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Timing, duration, reliability and predictability¦No additional intervention | 1 | 20% | 1 | 0.2 |  | Walcheren | Technical and operational readiness | Several companies already operate batteries with an Energy Management System. | Walcheren¦Technical and operational readiness
Schouwen-Duiveland | Grid operator | Speed and effect on reinforcement bridge gap | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Speed and effect on reinforcement bridge gap¦Conventional grid reinforcement | 1 | 20% | 1 | 0.2 |  | Walcheren | Legal, contractual and policy embeddedness | Base score unchanged for this criterion. | Walcheren¦Legal, contractual and policy embeddedness
Schouwen-Duiveland | Grid operator | Speed and effect on reinforcement bridge gap | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Speed and effect on reinforcement bridge gap¦Battery + EMS | 5 | 20% | 5 | 1 |  | Walcheren | Financial attractiveness | Companies view the option more favourably where it is cost-neutral and delivers usable connection capacity. ¦ The arrangement can reduce stress without requiring company-owned grid infrastructure. | Walcheren¦Financial attractiveness
Schouwen-Duiveland | Grid operator | Speed and effect on reinforcement bridge gap | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Speed and effect on reinforcement bridge gap¦Group Transport Agreement | 3 | 20% | 3 | 0.6 |  | Walcheren | Implementation speed and urgency fit | The solution can be implemented within the bridge period. | Walcheren¦Implementation speed and urgency fit
Schouwen-Duiveland | Grid operator | Speed and effect on reinforcement bridge gap | No additional intervention | -0.5 | No relief is provided during the bridge period; the baseline ATC stress remains 97.0%. | Percentage-based grid assessment | Schouwen-Duiveland¦Grid operator¦Speed and effect on reinforcement bridge gap¦No additional intervention | 2 | 20% | 1.5 | 0.3 |  | Walcheren | Knowledge and organisational burden | Battery and EMS operation is already established locally. ¦ Collective implementation is company-led, placing coordination work on participating companies. | Walcheren¦Knowledge and organisational burden
Schouwen-Duiveland | Grid operator | Technical and operational readiness | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Technical and operational readiness¦Conventional grid reinforcement | 5 | 15% | 5 | 0.75 |  | Walcheren | Autonomy and dependency | Base score unchanged for this criterion. | Walcheren¦Autonomy and dependency
Schouwen-Duiveland | Grid operator | Technical and operational readiness | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Technical and operational readiness¦Battery + EMS | 4 | 15% | 4 | 0.6 |  | Walcheren | Sustainability, image and strategic risk | Base score unchanged for this criterion. | Walcheren¦Sustainability, image and strategic risk
Schouwen-Duiveland | Grid operator | Technical and operational readiness | Group Transport Agreement | 0.5 | Regional energy cooperation is developing, which improves the relative readiness of a collective arrangement. | Interview synthesis | Schouwen-Duiveland¦Grid operator¦Technical and operational readiness¦Group Transport Agreement | 2 | 15% | 2.5 | 0.375 |  | West-Zeeuws-Vlaanderen | Grid-operator life-cycle cost and investment effect | The measured ATC stress decreases from 90.6% to 86.1%, below the 90% threshold. ¦ The measured ATC stress decreases from 90.6% to 85.8%, below the 90% threshold. | West-Zeeuws-Vlaanderen¦Grid-operator life-cycle cost and investment effect
Schouwen-Duiveland | Grid operator | Technical and operational readiness | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Technical and operational readiness¦No additional intervention | 2 | 15% | 2 | 0.3 |  | West-Zeeuws-Vlaanderen | Timing, duration, reliability and predictability | The available intervention information is not attributable to the analysed component. ¦ No operating collective arrangement is present and collective maturity is low. | West-Zeeuws-Vlaanderen¦Timing, duration, reliability and predictability
Schouwen-Duiveland | Grid operator | Legal, contractual and policy embeddedness | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Legal, contractual and policy embeddedness¦Conventional grid reinforcement | 4 | 15% | 4 | 0.6 |  | West-Zeeuws-Vlaanderen | Speed and effect on reinforcement bridge gap | The measured test clears the threshold with a 3.9-percentage-point margin. ¦ No intervention provides no relief while future coverage remains unresolved. | West-Zeeuws-Vlaanderen¦Speed and effect on reinforcement bridge gap
Schouwen-Duiveland | Grid operator | Legal, contractual and policy embeddedness | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Legal, contractual and policy embeddedness¦Battery + EMS | 3 | 15% | 3 | 0.45 |  | West-Zeeuws-Vlaanderen | Technical and operational readiness | No operating collective flexibility arrangement is present in the case. | West-Zeeuws-Vlaanderen¦Technical and operational readiness
Schouwen-Duiveland | Grid operator | Legal, contractual and policy embeddedness | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Legal, contractual and policy embeddedness¦Group Transport Agreement | 2 | 15% | 2 | 0.3 |  | West-Zeeuws-Vlaanderen | Legal, contractual and policy embeddedness | Base score unchanged for this criterion. | West-Zeeuws-Vlaanderen¦Legal, contractual and policy embeddedness
Schouwen-Duiveland | Grid operator | Legal, contractual and policy embeddedness | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Grid operator¦Legal, contractual and policy embeddedness¦No additional intervention | 5 | 15% | 5 | 0.75 |  | West-Zeeuws-Vlaanderen | Financial attractiveness | Batteries are already under consideration by companies in the case. ¦ The arrangement can reduce stress without requiring company-owned grid infrastructure. | West-Zeeuws-Vlaanderen¦Financial attractiveness
Schouwen-Duiveland | Company | Financial attractiveness | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Financial attractiveness¦Conventional grid reinforcement | 2 | 30% | 2 | 0.6 |  | West-Zeeuws-Vlaanderen | Implementation speed and urgency fit | The solution can be available before the unresolved reinforcement endpoint. | West-Zeeuws-Vlaanderen¦Implementation speed and urgency fit
Schouwen-Duiveland | Company | Financial attractiveness | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Financial attractiveness¦Battery + EMS | 5 | 30% | 5 | 1.5 |  | West-Zeeuws-Vlaanderen | Knowledge and organisational burden | New cooperation and governance would need to be created. | West-Zeeuws-Vlaanderen¦Knowledge and organisational burden
Schouwen-Duiveland | Company | Financial attractiveness | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Financial attractiveness¦Group Transport Agreement | 4 | 30% | 4 | 1.2 |  | West-Zeeuws-Vlaanderen | Autonomy and dependency | Central company decision structures increase dependency in a collective arrangement. | West-Zeeuws-Vlaanderen¦Autonomy and dependency
Schouwen-Duiveland | Company | Financial attractiveness | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Financial attractiveness¦No additional intervention | 2 | 30% | 2 | 0.6 |  | West-Zeeuws-Vlaanderen | Sustainability, image and strategic risk | Base score unchanged for this criterion. | West-Zeeuws-Vlaanderen¦Sustainability, image and strategic risk
Schouwen-Duiveland | Company | Implementation speed and urgency fit | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Implementation speed and urgency fit¦Conventional grid reinforcement | 1 | 20% | 1 | 0.2
Schouwen-Duiveland | Company | Implementation speed and urgency fit | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Implementation speed and urgency fit¦Battery + EMS | 4 | 20% | 4 | 0.8
Schouwen-Duiveland | Company | Implementation speed and urgency fit | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Implementation speed and urgency fit¦Group Transport Agreement | 3 | 20% | 3 | 0.6 |  | Scoring rules
Schouwen-Duiveland | Company | Implementation speed and urgency fit | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Implementation speed and urgency fit¦No additional intervention | 1 | 20% | 1 | 0.2 |  | Regional adjustment: −0.5, 0 or +0.5; editable in yellow cells.
Schouwen-Duiveland | Company | Knowledge and organisational burden | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Knowledge and organisational burden¦Conventional grid reinforcement | 4 | 20% | 4 | 0.8 |  | Adjusted score: MAX(1, MIN(5, base score + regional adjustment)).
Schouwen-Duiveland | Company | Knowledge and organisational burden | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Knowledge and organisational burden¦Battery + EMS | 3 | 20% | 3 | 0.6 |  | Actor score: weighted average of the five actor-specific criteria.
Schouwen-Duiveland | Company | Knowledge and organisational burden | Group Transport Agreement | 0.5 | Regional groups and municipal facilitation can reduce the coordination burden. | Interview synthesis | Schouwen-Duiveland¦Company¦Knowledge and organisational burden¦Group Transport Agreement | 2 | 20% | 2.5 | 0.5 |  | Overall score: equal average of the grid-operator and company scores.
Schouwen-Duiveland | Company | Knowledge and organisational burden | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Knowledge and organisational burden¦No additional intervention | 5 | 20% | 5 | 1 |  | Response options are the umbrella decision set; battery + EMS and the Group Transport Agreement are the flexibility-solution subset.
Schouwen-Duiveland | Company | Autonomy and dependency | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Autonomy and dependency¦Conventional grid reinforcement | 3 | 15% | 3 | 0.45
Schouwen-Duiveland | Company | Autonomy and dependency | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Autonomy and dependency¦Battery + EMS | 5 | 15% | 5 | 0.75
Schouwen-Duiveland | Company | Autonomy and dependency | Group Transport Agreement | 0.5 | Existing cooperation reduces the dependency objection identified by participating companies. | Interview synthesis | Schouwen-Duiveland¦Company¦Autonomy and dependency¦Group Transport Agreement | 2 | 15% | 2.5 | 0.375
Schouwen-Duiveland | Company | Autonomy and dependency | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Autonomy and dependency¦No additional intervention | 5 | 15% | 5 | 0.75
Schouwen-Duiveland | Company | Sustainability, image and strategic risk | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Sustainability, image and strategic risk¦Conventional grid reinforcement | 3 | 15% | 3 | 0.45
Schouwen-Duiveland | Company | Sustainability, image and strategic risk | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Sustainability, image and strategic risk¦Battery + EMS | 4 | 15% | 4 | 0.6
Schouwen-Duiveland | Company | Sustainability, image and strategic risk | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Sustainability, image and strategic risk¦Group Transport Agreement | 5 | 15% | 5 | 0.75
Schouwen-Duiveland | Company | Sustainability, image and strategic risk | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Schouwen-Duiveland¦Company¦Sustainability, image and strategic risk¦No additional intervention | 1 | 15% | 1 | 0.15
Walcheren | Grid operator | Grid-operator life-cycle cost and investment effect | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Grid-operator life-cycle cost and investment effect¦Conventional grid reinforcement | 2 | 30% | 2 | 0.6
Walcheren | Grid operator | Grid-operator life-cycle cost and investment effect | Battery + EMS | 0.5 | The measured ATC stress decreases from 94.8% to 88.3%, below the 90% threshold. | Percentage-based grid assessment | Walcheren¦Grid operator¦Grid-operator life-cycle cost and investment effect¦Battery + EMS | 4 | 30% | 4.5 | 1.35
Walcheren | Grid operator | Grid-operator life-cycle cost and investment effect | Group Transport Agreement | 0.5 | The measured ATC stress decreases from 94.8% to 89.1%, below the 90% threshold. | Percentage-based grid assessment | Walcheren¦Grid operator¦Grid-operator life-cycle cost and investment effect¦Group Transport Agreement | 4 | 30% | 4.5 | 1.35
Walcheren | Grid operator | Grid-operator life-cycle cost and investment effect | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Grid-operator life-cycle cost and investment effect¦No additional intervention | 5 | 30% | 5 | 1.5
Walcheren | Grid operator | Timing, duration, reliability and predictability | Conventional grid reinforcement | -0.5 | The component is already constrained and reinforcement follows only after a bridge period. | Public timing summary | Walcheren¦Grid operator¦Timing, duration, reliability and predictability¦Conventional grid reinforcement | 4 | 20% | 3.5 | 0.7
Walcheren | Grid operator | Timing, duration, reliability and predictability | Battery + EMS | 0.5 | The measured exceedance consists of short episodes, improving the fit of targeted storage dispatch. | Percentage-based grid assessment | Walcheren¦Grid operator¦Timing, duration, reliability and predictability¦Battery + EMS | 2 | 20% | 2.5 | 0.5
Walcheren | Grid operator | Timing, duration, reliability and predictability | Group Transport Agreement | -0.5 | Collective initiatives are at an early stage and are primarily focused on knowledge exchange. | Interview synthesis | Walcheren¦Grid operator¦Timing, duration, reliability and predictability¦Group Transport Agreement | 3 | 20% | 2.5 | 0.5
Walcheren | Grid operator | Timing, duration, reliability and predictability | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Timing, duration, reliability and predictability¦No additional intervention | 1 | 20% | 1 | 0.2
Walcheren | Grid operator | Speed and effect on reinforcement bridge gap | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Speed and effect on reinforcement bridge gap¦Conventional grid reinforcement | 1 | 20% | 1 | 0.2
Walcheren | Grid operator | Speed and effect on reinforcement bridge gap | Battery + EMS | 0.5 | The battery test clears the 90% threshold during the available bridge period. | Percentage-based grid assessment | Walcheren¦Grid operator¦Speed and effect on reinforcement bridge gap¦Battery + EMS | 5 | 20% | 5 | 1
Walcheren | Grid operator | Speed and effect on reinforcement bridge gap | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Speed and effect on reinforcement bridge gap¦Group Transport Agreement | 3 | 20% | 3 | 0.6
Walcheren | Grid operator | Speed and effect on reinforcement bridge gap | No additional intervention | -0.5 | No intervention leaves the measured ATC stress at 94.8% throughout the bridge period. | Percentage-based grid assessment | Walcheren¦Grid operator¦Speed and effect on reinforcement bridge gap¦No additional intervention | 2 | 20% | 1.5 | 0.3
Walcheren | Grid operator | Technical and operational readiness | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Technical and operational readiness¦Conventional grid reinforcement | 5 | 15% | 5 | 0.75
Walcheren | Grid operator | Technical and operational readiness | Battery + EMS | 0.5 | Several companies already operate batteries with an Energy Management System. | Interview synthesis | Walcheren¦Grid operator¦Technical and operational readiness¦Battery + EMS | 4 | 15% | 4.5 | 0.675
Walcheren | Grid operator | Technical and operational readiness | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Technical and operational readiness¦Group Transport Agreement | 2 | 15% | 2 | 0.3
Walcheren | Grid operator | Technical and operational readiness | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Technical and operational readiness¦No additional intervention | 2 | 15% | 2 | 0.3
Walcheren | Grid operator | Legal, contractual and policy embeddedness | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Legal, contractual and policy embeddedness¦Conventional grid reinforcement | 4 | 15% | 4 | 0.6
Walcheren | Grid operator | Legal, contractual and policy embeddedness | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Legal, contractual and policy embeddedness¦Battery + EMS | 3 | 15% | 3 | 0.45
Walcheren | Grid operator | Legal, contractual and policy embeddedness | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Legal, contractual and policy embeddedness¦Group Transport Agreement | 2 | 15% | 2 | 0.3
Walcheren | Grid operator | Legal, contractual and policy embeddedness | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Grid operator¦Legal, contractual and policy embeddedness¦No additional intervention | 5 | 15% | 5 | 0.75
Walcheren | Company | Financial attractiveness | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Financial attractiveness¦Conventional grid reinforcement | 2 | 30% | 2 | 0.6
Walcheren | Company | Financial attractiveness | Battery + EMS | 0.5 | Companies view the option more favourably where it is cost-neutral and delivers usable connection capacity. | Interview synthesis | Walcheren¦Company¦Financial attractiveness¦Battery + EMS | 5 | 30% | 5 | 1.5
Walcheren | Company | Financial attractiveness | Group Transport Agreement | 0.5 | The arrangement can reduce stress without requiring company-owned grid infrastructure. | Interview synthesis + percentage assessment | Walcheren¦Company¦Financial attractiveness¦Group Transport Agreement | 4 | 30% | 4.5 | 1.35
Walcheren | Company | Financial attractiveness | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Financial attractiveness¦No additional intervention | 2 | 30% | 2 | 0.6
Walcheren | Company | Implementation speed and urgency fit | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Implementation speed and urgency fit¦Conventional grid reinforcement | 1 | 20% | 1 | 0.2
Walcheren | Company | Implementation speed and urgency fit | Battery + EMS | 0.5 | The solution can be implemented within the bridge period. | Interview synthesis | Walcheren¦Company¦Implementation speed and urgency fit¦Battery + EMS | 4 | 20% | 4.5 | 0.9
Walcheren | Company | Implementation speed and urgency fit | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Implementation speed and urgency fit¦Group Transport Agreement | 3 | 20% | 3 | 0.6
Walcheren | Company | Implementation speed and urgency fit | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Implementation speed and urgency fit¦No additional intervention | 1 | 20% | 1 | 0.2
Walcheren | Company | Knowledge and organisational burden | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Knowledge and organisational burden¦Conventional grid reinforcement | 4 | 20% | 4 | 0.8
Walcheren | Company | Knowledge and organisational burden | Battery + EMS | 0.5 | Battery and EMS operation is already established locally. | Interview synthesis | Walcheren¦Company¦Knowledge and organisational burden¦Battery + EMS | 3 | 20% | 3.5 | 0.7
Walcheren | Company | Knowledge and organisational burden | Group Transport Agreement | -0.5 | Collective implementation is company-led, placing coordination work on participating companies. | Interview synthesis | Walcheren¦Company¦Knowledge and organisational burden¦Group Transport Agreement | 2 | 20% | 1.5 | 0.3
Walcheren | Company | Knowledge and organisational burden | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Knowledge and organisational burden¦No additional intervention | 5 | 20% | 5 | 1
Walcheren | Company | Autonomy and dependency | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Autonomy and dependency¦Conventional grid reinforcement | 3 | 15% | 3 | 0.45
Walcheren | Company | Autonomy and dependency | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Autonomy and dependency¦Battery + EMS | 5 | 15% | 5 | 0.75
Walcheren | Company | Autonomy and dependency | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Autonomy and dependency¦Group Transport Agreement | 2 | 15% | 2 | 0.3
Walcheren | Company | Autonomy and dependency | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Autonomy and dependency¦No additional intervention | 5 | 15% | 5 | 0.75
Walcheren | Company | Sustainability, image and strategic risk | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Sustainability, image and strategic risk¦Conventional grid reinforcement | 3 | 15% | 3 | 0.45
Walcheren | Company | Sustainability, image and strategic risk | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Sustainability, image and strategic risk¦Battery + EMS | 4 | 15% | 4 | 0.6
Walcheren | Company | Sustainability, image and strategic risk | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Sustainability, image and strategic risk¦Group Transport Agreement | 5 | 15% | 5 | 0.75
Walcheren | Company | Sustainability, image and strategic risk | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | Walcheren¦Company¦Sustainability, image and strategic risk¦No additional intervention | 1 | 15% | 1 | 0.15
West-Zeeuws-Vlaanderen | Grid operator | Grid-operator life-cycle cost and investment effect | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Grid-operator life-cycle cost and investment effect¦Conventional grid reinforcement | 2 | 30% | 2 | 0.6
West-Zeeuws-Vlaanderen | Grid operator | Grid-operator life-cycle cost and investment effect | Battery + EMS | 0.5 | The measured ATC stress decreases from 90.6% to 86.1%, below the 90% threshold. | Percentage-based grid assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Grid-operator life-cycle cost and investment effect¦Battery + EMS | 4 | 30% | 4.5 | 1.35
West-Zeeuws-Vlaanderen | Grid operator | Grid-operator life-cycle cost and investment effect | Group Transport Agreement | 0.5 | The measured ATC stress decreases from 90.6% to 85.8%, below the 90% threshold. | Percentage-based grid assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Grid-operator life-cycle cost and investment effect¦Group Transport Agreement | 4 | 30% | 4.5 | 1.35
West-Zeeuws-Vlaanderen | Grid operator | Grid-operator life-cycle cost and investment effect | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Grid-operator life-cycle cost and investment effect¦No additional intervention | 5 | 30% | 5 | 1.5
West-Zeeuws-Vlaanderen | Grid operator | Timing, duration, reliability and predictability | Conventional grid reinforcement | -0.5 | The available intervention information is not attributable to the analysed component. | Public uncertainty summary | West-Zeeuws-Vlaanderen¦Grid operator¦Timing, duration, reliability and predictability¦Conventional grid reinforcement | 4 | 20% | 3.5 | 0.7
West-Zeeuws-Vlaanderen | Grid operator | Timing, duration, reliability and predictability | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Timing, duration, reliability and predictability¦Battery + EMS | 2 | 20% | 2 | 0.4
West-Zeeuws-Vlaanderen | Grid operator | Timing, duration, reliability and predictability | Group Transport Agreement | -0.5 | No operating collective arrangement is present and collective maturity is low. | Interview synthesis | West-Zeeuws-Vlaanderen¦Grid operator¦Timing, duration, reliability and predictability¦Group Transport Agreement | 3 | 20% | 2.5 | 0.5
West-Zeeuws-Vlaanderen | Grid operator | Timing, duration, reliability and predictability | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Timing, duration, reliability and predictability¦No additional intervention | 1 | 20% | 1 | 0.2
West-Zeeuws-Vlaanderen | Grid operator | Speed and effect on reinforcement bridge gap | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Speed and effect on reinforcement bridge gap¦Conventional grid reinforcement | 1 | 20% | 1 | 0.2
West-Zeeuws-Vlaanderen | Grid operator | Speed and effect on reinforcement bridge gap | Battery + EMS | 0.5 | The measured test clears the threshold with a 3.9-percentage-point margin. | Percentage-based grid assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Speed and effect on reinforcement bridge gap¦Battery + EMS | 5 | 20% | 5 | 1
West-Zeeuws-Vlaanderen | Grid operator | Speed and effect on reinforcement bridge gap | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Speed and effect on reinforcement bridge gap¦Group Transport Agreement | 3 | 20% | 3 | 0.6
West-Zeeuws-Vlaanderen | Grid operator | Speed and effect on reinforcement bridge gap | No additional intervention | -0.5 | No intervention provides no relief while future coverage remains unresolved. | Public uncertainty summary | West-Zeeuws-Vlaanderen¦Grid operator¦Speed and effect on reinforcement bridge gap¦No additional intervention | 2 | 20% | 1.5 | 0.3
West-Zeeuws-Vlaanderen | Grid operator | Technical and operational readiness | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Technical and operational readiness¦Conventional grid reinforcement | 5 | 15% | 5 | 0.75
West-Zeeuws-Vlaanderen | Grid operator | Technical and operational readiness | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Technical and operational readiness¦Battery + EMS | 4 | 15% | 4 | 0.6
West-Zeeuws-Vlaanderen | Grid operator | Technical and operational readiness | Group Transport Agreement | -0.5 | No operating collective flexibility arrangement is present in the case. | Interview synthesis | West-Zeeuws-Vlaanderen¦Grid operator¦Technical and operational readiness¦Group Transport Agreement | 2 | 15% | 1.5 | 0.225
West-Zeeuws-Vlaanderen | Grid operator | Technical and operational readiness | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Technical and operational readiness¦No additional intervention | 2 | 15% | 2 | 0.3
West-Zeeuws-Vlaanderen | Grid operator | Legal, contractual and policy embeddedness | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Legal, contractual and policy embeddedness¦Conventional grid reinforcement | 4 | 15% | 4 | 0.6
West-Zeeuws-Vlaanderen | Grid operator | Legal, contractual and policy embeddedness | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Legal, contractual and policy embeddedness¦Battery + EMS | 3 | 15% | 3 | 0.45
West-Zeeuws-Vlaanderen | Grid operator | Legal, contractual and policy embeddedness | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Legal, contractual and policy embeddedness¦Group Transport Agreement | 2 | 15% | 2 | 0.3
West-Zeeuws-Vlaanderen | Grid operator | Legal, contractual and policy embeddedness | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Grid operator¦Legal, contractual and policy embeddedness¦No additional intervention | 5 | 15% | 5 | 0.75
West-Zeeuws-Vlaanderen | Company | Financial attractiveness | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Financial attractiveness¦Conventional grid reinforcement | 2 | 30% | 2 | 0.6
West-Zeeuws-Vlaanderen | Company | Financial attractiveness | Battery + EMS | 0.5 | Batteries are already under consideration by companies in the case. | Interview synthesis | West-Zeeuws-Vlaanderen¦Company¦Financial attractiveness¦Battery + EMS | 5 | 30% | 5 | 1.5
West-Zeeuws-Vlaanderen | Company | Financial attractiveness | Group Transport Agreement | 0.5 | The arrangement can reduce stress without requiring company-owned grid infrastructure. | Interview synthesis + percentage assessment | West-Zeeuws-Vlaanderen¦Company¦Financial attractiveness¦Group Transport Agreement | 4 | 30% | 4.5 | 1.35
West-Zeeuws-Vlaanderen | Company | Financial attractiveness | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Financial attractiveness¦No additional intervention | 2 | 30% | 2 | 0.6
West-Zeeuws-Vlaanderen | Company | Implementation speed and urgency fit | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Implementation speed and urgency fit¦Conventional grid reinforcement | 1 | 20% | 1 | 0.2
West-Zeeuws-Vlaanderen | Company | Implementation speed and urgency fit | Battery + EMS | 0.5 | The solution can be available before the unresolved reinforcement endpoint. | Interview synthesis | West-Zeeuws-Vlaanderen¦Company¦Implementation speed and urgency fit¦Battery + EMS | 4 | 20% | 4.5 | 0.9
West-Zeeuws-Vlaanderen | Company | Implementation speed and urgency fit | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Implementation speed and urgency fit¦Group Transport Agreement | 3 | 20% | 3 | 0.6
West-Zeeuws-Vlaanderen | Company | Implementation speed and urgency fit | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Implementation speed and urgency fit¦No additional intervention | 1 | 20% | 1 | 0.2
West-Zeeuws-Vlaanderen | Company | Knowledge and organisational burden | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Knowledge and organisational burden¦Conventional grid reinforcement | 4 | 20% | 4 | 0.8
West-Zeeuws-Vlaanderen | Company | Knowledge and organisational burden | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Knowledge and organisational burden¦Battery + EMS | 3 | 20% | 3 | 0.6
West-Zeeuws-Vlaanderen | Company | Knowledge and organisational burden | Group Transport Agreement | -0.5 | New cooperation and governance would need to be created. | Interview synthesis | West-Zeeuws-Vlaanderen¦Company¦Knowledge and organisational burden¦Group Transport Agreement | 2 | 20% | 1.5 | 0.3
West-Zeeuws-Vlaanderen | Company | Knowledge and organisational burden | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Knowledge and organisational burden¦No additional intervention | 5 | 20% | 5 | 1
West-Zeeuws-Vlaanderen | Company | Autonomy and dependency | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Autonomy and dependency¦Conventional grid reinforcement | 3 | 15% | 3 | 0.45
West-Zeeuws-Vlaanderen | Company | Autonomy and dependency | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Autonomy and dependency¦Battery + EMS | 5 | 15% | 5 | 0.75
West-Zeeuws-Vlaanderen | Company | Autonomy and dependency | Group Transport Agreement | -0.5 | Central company decision structures increase dependency in a collective arrangement. | Interview synthesis | West-Zeeuws-Vlaanderen¦Company¦Autonomy and dependency¦Group Transport Agreement | 2 | 15% | 1.5 | 0.225
West-Zeeuws-Vlaanderen | Company | Autonomy and dependency | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Autonomy and dependency¦No additional intervention | 5 | 15% | 5 | 0.75
West-Zeeuws-Vlaanderen | Company | Sustainability, image and strategic risk | Conventional grid reinforcement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Sustainability, image and strategic risk¦Conventional grid reinforcement | 3 | 15% | 3 | 0.45
West-Zeeuws-Vlaanderen | Company | Sustainability, image and strategic risk | Battery + EMS | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Sustainability, image and strategic risk¦Battery + EMS | 4 | 15% | 4 | 0.6
West-Zeeuws-Vlaanderen | Company | Sustainability, image and strategic risk | Group Transport Agreement | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Sustainability, image and strategic risk¦Group Transport Agreement | 5 | 15% | 5 | 0.75
West-Zeeuws-Vlaanderen | Company | Sustainability, image and strategic risk | No additional intervention | 0 | Base score unchanged for this case. | Base TAPIR assessment | West-Zeeuws-Vlaanderen¦Company¦Sustainability, image and strategic risk¦No additional intervention | 1 | 15% | 1 | 0.15

## Read Me
Read Me — Public TAPIR Decision-Support Tool
This clean public workbook preserves the decision-support logic while removing confidential grid-operator asset and load information.
How to use
1. Open the Public Tool sheet and select one of the three case regions in the yellow case selector.
2. Review the four response-option scores (one decimal place in every case), the compact village and two-station context block, and the criterion-level evidence., the public village demand indicators, the percentage-only load indicators for the two station levels and the case-specific evidence.
3. If sensitivity testing is required, edit only the yellow weight, base-score and regional-adjustment cells on Public Inputs.
Terminology used
Response option is the umbrella term for the alternatives assessed by the tool: conventional grid reinforcement, battery + EMS, Group Transport Agreement and no additional intervention.
Flexibility solutions are the response-option subset that uses demand, generation or storage flexibility within available grid capacity: battery + EMS and the Group Transport Agreement.
Grid reinforcement is not a flexibility solution. No additional intervention is the reference response option.
Public anonymisation applied
The three village names have been replaced by the non-identifying labels Village 1, Village 2 and Village 3, but the measured village demand indicators themselves are public and are shown in full.
All station names, abbreviations, codes, addresses and connected-asset identifiers have been removed and replaced by generic grid-component descriptions.
All absolute station load, capacity and relief values have been removed. Station stress is published only as a percentage of available transport capacity (ATC), for the 2025 and 2031 reference years, together with the first constraint year, the critical hours at or above 90% and the holiday share of those hours.
Exact reinforcement costs, capacities and dates, internal source filenames and recoverable raw-data tables have been removed.
The workbook has no hidden worksheets, external links, charts linked to confidential data or embedded source files.
Evidence retained
General case findings from the thesis and interviews are retained where they explain maturity, coordination, authority, organisational burden and company preferences.
Grid evidence is retained only in normalised percentage form and is labelled as measured, forecast or uncertain.
Grid evidence is retained only in normalised percentage form and is labelled as measured, forecast or unresolved. Village demand evidence is retained in full because it is not confidential.
Limitations
The public percentages support comparison but cannot reproduce the grid operator's internal calculations because the absolute source data have deliberately been removed.
A preferred response option is a decision-support result, not an automatic investment decision. Local engineering validation, legal assessment and actor agreement remain necessary.
Flexibility may complement reinforcement or bridge a period until reinforcement is completed; it is not presumed to substitute for physical capacity expansion.
Source basis: thesis Chapters 5–8, thesis case documents and the interview evidence already used in the thesis. Public release prepared without absolute grid-operator load or asset data.